MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

NORTH HAVEN WATER DEPARTMENT

FRESH POND WATERSHED

MARCH 2003

prepared for

Source Water Assessment Program

Drinking Water Program

Maine Department of Human Services

prepared by

Drumlin Environmental, LLC

Portland, Maine

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

NORTH HAVEN WATER DEPARTMENT

FRESH POND WATERSHED

MARCH 2003

prepared for

Source Water Assessment Program

Drinking Water Program

Maine Department of Human Services

11 State House Station

Augusta, Maine  04333

prepared by

Drumlin Environmental, LLC

15 Franklin Street, P. O. Box 392

Portland, Maine 04112-0392

(207) 771-5546

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

NORTH HAVEN WATER DEPARTMENT

FRESH POND WATERSHED

# TABLE OF CONTENTS

Section      Title                                                                                                            Page No.

|  | EXECUTIVE SUMMARY | ii |
| --- | --- | --- |
| 1.0 | INTRODUCTION | 1 |
| 2.0 | WATER SUPPLY SOURCE | 1 |
|  | 2.1 Description | 1 |
|  | 2.2 Land Use | 3 |
| 3.0 | INVENTORY OF POTENTIAL WATER QUALITY CONCERNS | 4 |
|  | 3.1 Background | 4 |
|  | 3.2 Source Sensitivity to Land Use | 5 |
| 4.0 | # ASSESSMENT OF FRESH POND | 5 |
|  | 4.1 Watershed | 6 |
|  | 4.2 Shoreland | 6 |
|  | 4.3 Intake | 6 |
| 5.0 | SWAP RANKING AND RECOMMENDATIONS | 7 |
|  | 5.1 Ranking of Susceptibility | 7 |
|  | 5.2 Recommendations | 8 |
|  | Table 1 - Fresh Pond Supply | 2 |
|  | Table 2 - Sources of SWAP Information | 5 |
|  | Table 3 - Fresh Pond Surface Water Assessment | 7 |
|  | Figure 1 - Public Water Supply and Surrounding Watershed | End |
|  | Figure 2 - Multi-Resolution Land Characterization | End |
|  | Figure 3 - Potential Threats to Drinking Water | End |
|  | Figure 4 - Potential Erodible Soils | End |
|  | Appendix A - SWAP Assessment Guidelines | End |

NORTH HAVEN WATER DEPARTMENT

# FRESH POND WATERSHED

# EXECUTIVE SUMMARY

The North Haven Water Department serves approximately 300 people from Fresh Pond and more than 1,000 in the summer with the influx of seasonal residents and visitors.  The water supply operated under a filtration waiver until 1996 when the waiver was revoked due to water quality concerns.   The Water Department is now working on plans to build a new water filtration plant.

The 1,072-acre watershed of Fresh Pond is located in the center of the island of North Haven.  There are no significant stream drainages that discharge into the pond.  The pond is relatively small and shallow.  Approximately 85 percent of the watershed is in forest growth.  Large wetland areas are located at the north and south ends of the pond.   The decay of wetland vegetation affects the color of water in the pond.

The shoreland is undeveloped and protected by local zoning.  A camp and a few residential homes are the only existing development near the pond.  The upland watershed is mostly in natural growth with limited low-density development located along the roadways, and is also protected by local zoning.   Access is provided to the pond by the Water Department’s service road to the intake and pump station.  A second access point from Middle Road is used for recreation activities on the pond.

No significant land use threats were identified from existing databases or during the reconnaissance of the watershed.  A fuel storage tank located at the pump station is contained although contingency measures for spill prevention are needed.   The principal activities to monitor in the watershed include recreational use and the potential for future residential development.   The pond is eutrophic and thus is sensitive to further degradation from runoff.

The overall susceptibility of the Fresh Pond water supply is ranked as low to moderate.

Low susceptibility is based on the low density of development in the watershed, zoning controls, the predominantly forested cover and the lack of potential threats from land use activities.  The moderate susceptibility ranking is based on the absence of ownership control, the presence of the AST fuel storage tank and the natural state of the pond (i.e., eutrophic state, high color and limited buffering capacity).

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

NORTH  HAVEN WATER DEPARTMENT

# FRESH POND WATERSHED

1.0    INTRODUCTION

The operation of public water systems in Maine is governed by the federal Safe Drinking Water Act (SDWA), which was first passed in the 1970s and later amended in 1986 and 1996.   The federal government delegated authority for enforcing the SDWA to the state under the Maine Department of Human Services (DHS) Drinking Water Program (DWP).   In 1998, the Source Water Protection Section was established in the DWP to implement the Maine Public Drinking Water Source Water Assessment Program (SWAP).   The SWAP process is being conducted through a cooperative effort between the DWP staff, North Haven Water Department (Water Department) staff and Drumlin Environmental, LLC (Drumlin), the environmental consulting firm contracted through DHS to provide technical assistance for the project.

The purpose of the SWAP evaluation for the Water Department is to assess the susceptibility of its Fresh Pond drinking water supply (PWSID  91130) to potential threats of contamination.   The long-term goal is to protect the water supply source.   To do this, the SWAP process has compiled information to assist the Water Department in future planning that will help to control potential threats to the water quality of Fresh Pond.

This Report describes the SWAP for the North Haven Water Department and is organized as follows:

- Section 2.0  summarizes the physical characteristics of the water supply at Fresh Pond;

- Section 3.0  describes the variety of conditions and activities that could pose a threat to water quality;

- Section 4.0  provides an assessment of the threats within the Fresh Pond watershed; and,

- Section 5.0  ranks the susceptibility of the water quality at Fresh Pond and provides recommendations for future protection of water quality.

2.0   WATER SUPPLY SOURCE

2.1   Description

The Fresh Pond watershed is located on the island of North Haven.  The island is approximately 10.5 square miles in area.  The pond and watershed area are located in the central portion of the island, which is relatively undeveloped (shown in Figure 1).  The pond outlet is located at the mid-point of the pond along the northwest shoreline.   The outlet is controlled by a man-made dam, which was constructed to maintain a higher, more constant level in the pond.   Marsh wetlands occur at the northeast and southwest ends of the pond and are a primary source of organic decomposition in the pond.  The components and description of the Water Department source are presented below in Table 1.

# TABLE 1

# FRESH POND SUPPLY

| # Category | # Description |
| --- | --- |
| Water System Name: | North Haven Water Department |
| Surface Water Source(s): | Fresh Pond |
| Water System Type: | Non-transient, community system |
| Watershed Location: | North Haven, Maine |
| Source Surface Water Area: | 101 Acres |
| Source Watershed Area: | 1,072 Acres |
| Average/Maximum Depths (estimated): | 9 ft; 14 ft |
| Water Volume in Storage: | undetermined |
| Population Served (customers): | Services: 128 year round; 170 summer Population: Approx. 300; > 1,000 in summer |
| Type of Treatment: | Chlorination (presently) Pre-Ozonation, Slow Sand Filtration and Corrosion Control |
| Filtration: | Filtration waiver revoked by State thus new treatment system to be constructed. |
| Estimated Daily Water Use: | Summer: 108,300 GPD average Winter: 24,500 GPD average |

The North Haven water system was constructed in 1910.   The water supply has consisted of a raw water pumping station, disinfection, 250,000-gallon standpipe and pipeline distribution system.   The system operated historically until 1996 under the provisions of a filtration waiver.   Occasional spikes of coliform bacteria and high color caused by the decay of naturally occurring organics resulted in the waiver being revoked by the State Drinking Water Program.   The Water Department is currently working with an engineering firm to develop a water treatment facility design to bring the Fresh Pond supply into compliance with drinking water regulations.   The preliminary design identified a treatment facility to include pre-ozonation, slow sand filtration, disinfection and corrosion control.   At the time of this report, final design plans were being prepared.

The Water Department intake is positioned within about 65 feet offshore at the south end of the pond.   The three- or four-inch diameter intake pipe is located near the pond bottom at a depth of approximately 10 feet below the water surface.  The intake is not marked with buoys or signs to indicate its exact location.   The pump station, located near the shore of the pond, draws water from the intake pipe and subsequently flows into the distribution system.   As water flows through the pump station, sodium hypochlorite is added for chlorination.   Contact time is provided as the water flows in the 6-inch main that is located at the start of the distribution system.

2.2   Land Use

The Water Department does not own or control any significant land area around the pond or in the upland watershed.   The Water Department ownership is limited to a small one-half acre parcel where the pump station is located at the southern end of the pond.  The remaining land around the pond and in the watershed is owned privately.

The watershed is protected by three local ordinance provisions.  North Haven has adopted the state’s version of the Shoreland Zone Ordinance (250-ft setback) for the shore around the pond.  In addition, protection is provided to the shoreland through North Haven’s Land Use and Subdivision Control Ordinance.  Under the provisions of the Resource Protection Zone, no new development is allowed within 600 feet of the pond shoreline and no motor-powered uses are allowed on the pond.  Existing structures within this zone are considered non-conforming and subject to review by the Planning Board for any added development.   According to the town administrator, there are only three developed residential properties and one camp located near the pond.   Outside the 600-ft zone, land uses are subject to the Fresh Pond Watershed Protection Ordinance.   This ordinance provides for a minimum number of allowed uses and controls or prohibits other uses that pose a potential threat to water resources.

No buildings or other development are located along the shore of Fresh Pond other than the pump station for the water supply.   The road to the pump station is the only roadway access to the pond.   The access to the pond is marked with a sign indicating the presence of the water supply.   The pond can be accessed across private property in one other location on the north side from Middle Road where the road is close to the pond.   This access is used on occasion to launch canoes, which is an allowed recreational activity on the pond.   A sign was posted at the access point to prohibit swimming and other contact recreation although the sign was not observed at the time of the site visit for SWAP.

The Fresh Pond watershed contains low intensity residential development and limited roadways.  Approximately 85 percent of the watershed is evergreen, deciduous and mixed forest growth.  Wetlands, limited pasture and wild grasses comprise most of the remaining area (12%) other than roadways and residential lots.  Emergent wetlands and swamp areas are present at the north and south ends of the pond.   A map of the land use classifications for the watershed and surrounding area is shown in Figure 2.   Farming is limited to a few grazing animals located on one property in the watershed.   Forestry cutting is not active in the watershed other than occasional harvesting for firewood.

There is no formal public access for recreational activities on the pond.  However, access can be obtained with permission across private land from Middle Road for canoeing and fishing.  Swimming and motorboats are not allowed on the pond.  Recreational vehicles and snowmobiles may use areas near the pond although such activities are limited and no problems are known to exist which would be a cause of concern to the water supply.

3.0   INVENTORY OF POTENTIAL WATER QUALITY CONCERNS

### 3.1   Background

### The Source Water Assessment Program (SWAP) is intended to assist water companies and departments in protecting the quality of their surface water supply by identifying potential threats to water quality.  Two factors have been considered in identifying and assessing the potential risk posed by a threat: (a) location in relation to the intake and (b) the nature of a potential threat.

This SWAP assessment looks for potential threats to water quality in three zones:

- The intake zone within 1,000 feet of the intake;

- The shoreline zone, within 250 feet of the shoreline of the surface water body; and,

- The watershed zone, extending to the limits of the surface watershed.

Activities in each of these zones have a different potential effect on the quality of water in the surface supply.

Within each of the three zones, the SWAP assessment examined a variety of conditions, land uses and practices that have a potential to influence water quality.  These features generally fall into one of the following categories:

- Physical characteristics of the watershed, for example the presence of wetlands, steep topography or erodible soils;

- General land uses and development patterns, for example the percentage of developed versus undeveloped land and controls to guide future development; and,

- Specific activities that involve chemical handling or may release pathogens (e.g., fecal coliform) with the potential to degrade water quality.

The SWAP assessment also considered available water quality data from the surface supply as an indicator of existing conditions.  Appendix A describes specific guidance used during the SWAP to inventory potential factors influencing water quality.  Appendix A also lists specific activities included in the SWAP assessment.  Table 2 lists general sources of information consulted during SWAP research.

# TABLE 2

SOURCES OF SWAP INFORMATION

| Information Type | Information Source |
| --- | --- |
| Watershed Characteristics | US Geological Survey (Topography, Hydrology), Soil Conservation Service (Soils), Maine Geological Survey (Geology) |
| Raw Water Quality | Water Department Monitoring |
| Potential Contamination Sources | DEP Databases and Water Department |
| Land Use and Zoning | Water Department and Municipal Records |
| Other Analyses | Other DEP Databases |

3.2  Source Sensitivity to Land Use

The key watershed features that define the sensitivity of the water supply source to land uses are briefly described below:

- Natural Features:   The watershed is largely forested.  Farming and wood cutting occur as minor activities in the watershed.   The natural, undeveloped watershed conditions are protective of the water supply source.   Wetlands located at the north and south ends of the pond, however, are a source of organic matter and natural decay that can affect pond water quality.

- Man-made Features:   Only a few residential homes exist near the pond and the density of residential development in the upland watershed is low.   Local zoning controls are restrictive on development within the watershed and prohibitive on development within 600 feet of the pond shoreline.

- Specific Activities:   Access to the pond shoreland for public recreation is limited by the lack of roadways and trails near the pond and by private land ownership.  The pond is accessed on occasion across private land for fishing and canoeing.

4.0   ASSESSMENT OF FRESH POND

Fresh Pond was used in the past as an unfiltered, chlorinated water supply source.   Historically, the water quality was acceptable for use under a filtration waiver.   Raw water test records (i.e., TE2 & TE3) maintained by the Water Department show all parameters were within acceptable standards for public drinking water.   However, occasional problems with coliform bacteria and color caused by decaying organic matter have caused the Water Department to relinquish the filtration waiver and develop plans for construction of a water treatment system.

4.1   Watershed

Fresh Pond and its watershed are of relatively small size with no significant stream drainages flowing into the pond.  Because of the shallow depth of the pond, the amount of water in storage is limited and the capacity to buffer potential land use impacts on runoff flowing into the pond is limited.  Land use in the watershed is comprised of a low-density residential development, minor farming and no active, larger-scale forest harvesting.  The watershed is protected by a local ordinance, which controls the types of land use and development that are allowed in the watershed.

Review of the DEP databases of regulated activities and observations made during our reconnaissance of the watershed found no significant point or non-point sources of potential contamination that would be a concern to the water supply.   The databases show a petroleum storage tank removed from the North Haven Community School and a municipal sludge spreading site both of which are remote from the water supply at the boundary of the watershed.  In addition, a grass landing strip is located near the southwestern watershed boundary.  This landing strip is used on a limited basis to deliver mail to the island in months when the weather is good for flying.  No building, maintenance or fueling facilities are present at the landing strip.  The locations of these sites relative to the water supply and intake are shown in Figure 3.

4.2   Shoreland

The shoreland is undeveloped and in natural field, wetland and forest growth.  The shoreland is protected by shoreland zoning (up to 250 feet) and the land use/subdivision control ordinance (up to 600 feet) from the shore.  A few residential homes and a private camp set back from the pond shore represent the only development near the pond other than the Water Department intake pump station.

The shoreland topography around the pond varies from gentle to steep slopes.  The forested, undeveloped slopes around the pond are generally not subject to erosion.  Soils found on steep slopes are sensitive to erosion, if disturbed (see Figure 4).   The steepest slopes and highest potential for erosion occur along the southern shore of the pond.

4.3   Intake

The water supply intake is located in the pond approximately 65 feet from shore.  The intake is not presently identified by signs or buoys.   Recreational activity on the pond is reported to be minor and infrequent, and to date has not become a problem or concern to the Water Department.  Testing of raw water collected from the pond at the intake has shown acceptable drinking water quality for TE2 and TE3 parameters.   The Water Department uses an aboveground oil storage tank (AST), which is located in the pump station.  The tank is equipped with secondary containment in the event of a leak or spill.

Lakes and ponds normally experience an aging process known as eutrophication, which is caused by various natural and man-made influences.   Phosphorus from runoff, fertilizers, sewage and other sources is a primary factor affecting eutrophication since phosphorus nourishes plant and algae growth in the pond.   The amount of algae productivity in the pond is characterized in terms of three Trophic States: (1) Oligotrophic = low, (2) Mesotrophic = moderate, and (3) Eutrophic = high.  The Trophic State can be identified based on chlorophyll and phosphorus content and by secchi disk transparency data, which measures the clarity of the pond water.  The results of historical turbidity testing show low turbidity generally below 1.2 NTUs.   On occasion, a higher peak reading was recorded due to spring runoff, high winds and/or pond turnover.  The factors that lead to the surrender of the filtration waiver included exceedence of allowable coliform bacteria concentrations and elevated color due to natural organics from decaying vegetation.

According to a surface water classification database developed by the DEP, the Trophic State of Fresh Pond is listed as Eutrophic.  The pond water is ranked as fully attaining the GPA classification with respect to primary contact, aquatic life and trophic stability criteria.

5.0   SWAP RANKING AND RECOMMENDATIONS

5.1   Ranking of Susceptibility

The SWAP assessment factors indicate that overall susceptibility of the water quality in Fresh Pond is low to moderate with respect to potential impacts from man-made land uses and activities.  Low susceptibility is based on the general conditions observed, including the low density of development in the watershed, zoning controls, the predominantly forested cover and the lack of potential threats from land use activities.  The moderate susceptibility ranking is based on the absence of ownership control, the presence of the AST fuel storage tank and the natural state of the pond.  These natural conditions include its eutrophic state, the decay of organic matter causing high color, the shallow depths which limit the amount of water available to buffer high color concentrations; and, the lack of any significant streamflow for flushing organic matter and color out of the pond.

Specific factors considered in assessing the overall risk are summarized in Table 3.

# TABLE  3

# FRESH POND SURFACE WATER ASSESSMENT

| Zone | Measure | Findings | Risk Level |
| --- | --- | --- | --- |
| Watershed | Ambient Water Quality Existing Conditions Future Development Overall | Class GPA, in full compliance. Land use characteristics present a low threat to water quality; public awareness for protecting the resource is high. Future development is controlled by various zoning ordinances; pressure for future development is low. | Low Low Low Low |
| Shoreland | Pond Classification Soils Activities Posing a Threat Potential for Future Threats Overall | Eutrophic-pond is more sensitive to the quality of near-shore runoff. Potentially erodible soils on steep slopes; Lyman (15-45%), Boothbay (15-25%). Limited access and public use for recreation (e.g., canoeing and fishing). Protection relies primarily on zoning controls for privately owned land; direct ownership and access control by Water Department is minimal. | High Low-Moderate Low Low-Moderate Low-Moderate |
| Intake | Raw Water Quality Ownership/Control Activities Posing a Threat Potential for Future Threats Overall | TE2 & TE3 testing shows good quality; filtration waiver lost due to bacteria and high color concentrations. Water Department ownership protection of intake area is minimal. Public access to intake area is unrestricted; AST fuel storage at pump station. Increased public use on pond. | Low-Moderate Low-Moderate Low-Moderate Low Low |
| Overall |  |  | Low-Moderate |

5.2   Recommendations

The overall ranking for the pond susceptibility to threats of contamination is low to moderate.  Several additional actions could be considered by the Water Department and the town to provide added protection to the quality of the water supply.

- A spill contingency plan should be developed to address the threat of an oil spill when fuel is delivered to the storage tank located in the pump station.   The plan should address precautions to be taken during fuel deliveries and identify the equipment and procedures to be used in the event of a spill.   The future need and provisions of the contingency plan may change with the construction of the new water filtration plant.

- Zoning controls enhance the protection of the shoreland and watershed areas.   However, ownership and conservation easements under the control of the Water Department provide the greatest protection strategy for long-term conservation of the water resource.   The Water Department should pursue a long-term plan to work with local landowners to develop and implement opportunities for gifts or purchase of land and easements.

- The pond can be accessed from Middle Road for recreational activities.   The Water Department should work with the landowner to inform the public about the water supply and activities allowed on the pond (e.g., through signs, pamphlets or other means).

APPENDIX A

#### SWAP ASSESSMENT GUIDELINES

MAINE PUBLIC DRINKING WATER

SOURCE WATER ASSESSMENT PROGRAM

NORTH HAVEN WATER DEPARTMENT

FRESH POND WATERSHED

# APPENDIX A

# ASSESSMENT GUIDELINES

| Assessment Item/Threat | Low | Moderate | Significant |
| --- | --- | --- | --- |
| Physical Characteristics of the Watershed Watershed boundary, area Area of water body Tributaries Watershed topography Wetlands Water body depth Sand and gravel aquifers Soil types (erodibility and slope) | smaller smaller few low many deep few low | >> >> >> moderate >> >> some moderate | larger larger many steep, rugged few shallow many high |
| Raw Water Quality Secchi Disk Transparency Turbidity pH Phosphorus Pesticides and herbicides Color Total Coliform and E Coli Dissolved Oxygen Temperature VOCs Chlorophyll-a Total Organic Carbon | > 8 M < 1 NTU 6.5-8.5 < 10 ppb ND < 5 > 29/100 ml >7 mg/L ambient absent < 2 ppb < 4 mg/L | 4-8 M < 5 NTU N/A < 20 ppb N/A 5-15 occasional 5-7 mg/L N/A 2-6 ppb 4-8 mg/L | < 4 M > 5 NTU < 6.5 or > 8.5 > 30 ppb detected > 15 > 142/100 ml < 5 mg/L > 10o C ambient detected > 6 ppb > 8 mg/L |
| Potential Contamination Source Inventory UST/AST leak sites Municipal/Comm/Special Landfill Compost sites Demolition debris sites Ash/septage storage/utilization Superfund site Sand/salt storage sites Petroleum spill sites Hazardous waste sites Wastewater treatment facilities Food residuals utilization sites Uncontrolled hazardous sites Tank farms Industrial complexes | Absent from watershed or actively monitored and controlled or fully remediated. | Present in watershed, some operational deficiencies and/or remediation is underway. | Present and unmonitored and/or unremediated. |

| Assessment Item/Threat | Low | Moderate | Significant |
| --- | --- | --- | --- |
| Potential Contamination Source Inventory Non-point pollution sources Transfer stations Sludge utilization sites Automobile graveyards Engineered subsurface systems Woodyards Underground injection wells Surface impoundments Mining/mineral processing sites Overboard discharges to rivers Active UST sites Roadways Railroads Utility Rights-of-way Boat launches Commercial farms CAFOs Commercial forest operations Private septic systems Home heating oil tanks Airports Bathing beaches Combined sewage overflows | If present, at low density, properly installed and operated. In compliance with applicable local, state and federal regulations. | >>>> | High density, little evidence of active management, documented incidence of problems and failures. |
| Land Uses and Zoning Residential density Percent of watershed Owned by PWS Public lands or conservation Forested With protective zoning Agricultural Impervious cover Industrial/commercial Waterbody uses: Restricted areas Ice fishing Boating Swimming Recreational vehicles | > 2 Ac/lot total > 80% for all protected uses < 20 % total < 20 % total < 20 % total large, posted limited to absent | 1-2 Ac/lot intake and shoreland protected, others developed 20-30% total 20-30% total 20-30% total intake zone moderate, well-managed | < 1 Ac/lot critical areas (intake, shoreland) unprotected or developed > 30% total of 3 > 30% total of 3 > 30% total of 3 small to none prevalent, uncontrolled |
| Other Analyses Trophic State Index Vulnerability Index Build-out Analysis | < 25 low fully developed | 25-60 moderate >>> | > 60 high high potential for development |