## System Losses
CMP System Losses
(These system losses exclude losses over PTF facilities)
Loss Factors by Voltage Level
|  | Winter | Non-Winter | Average
| Secondary | 0.078346 | 0.082998 | 0.081299
| Primary | 0.040232 | 0.040236 | 0.040785
| Sub-Transmission | 0.013918 | 0.015085 | 0.014599
| Transmission | 0.002351 | 0.003379 | 0.003017
Weighted Average Loss Factors by Class*
(Based on 2012 data)
|  |  | 2014 |  | YTD June 2015
Medium Class |  |  | Total Class | SO Only | Total Class | SO Only
| % of Class @ Secondary Voltage |  | 96.2% | 96.5% | 96.5% | 96.8%
| % of Class @ Primary Voltage |  | 3.8% | 3.5% | 3.5% | 3.2%
|  |  | 100% | 100% | 100% | 100%
Medium Class Weighted Average Loss Factor |  |  | 0.079759 | 0.079881 | 0.079881 | 0.080003
|  |  | 2014 |  | YTD June 2015
Large Class |  |  | Total Class | SO Only | Total Class | SO Only
| % of Class @ Secondary |  | 19.4% | 46.8% | 20.8% | 29.7%
| % of Class @ Primary |  | 27.1% | 20.5% | 29.2% | 22.6%
| % of Class @ Sub-Transmission |  | 26.1% | 31.2% | 26.6% | 38.3%
| % of Class @ Transmission |  | 27.4% | 1.5% | 23.5% | 9.4%
|  |  | 100% | 100% | 100% | 100%
Large Class Weighted Average Loss Factor |  |  | 0.031462 | 0.051009 | 0.033412 | 0.039238
Application of Loss Factors
Total MWh to be provided = (1+loss factor) x (MWh measured at meter)
* - Note: Nearly all of the Small Class is served at Secondary Voltage