## A
BHE System Losses
(These system losses exclude losses over PTF facilities)
Loss Factors by Voltage Level
Average
|  | Secondary | 0.10988
|  | Primary | 0.059547
|  | Sub-Transmission | 0.030715
|  | Transmission | 0.016157
Weighted Average Loss Factors by Class
(Based on 2004 Usage)
Medium Class |  |  | Total Class | SO Only
|  | % of Class @ Secondary Voltage | 83.49% | 85.41%
|  | % of Class @ Primary Voltage | 16.51% | 14.59%
|  |  | 100% | 100%
Medium Class Weighted Average Loss Factor |  |  | 0.10153 | 0.10253
Large Class |  |  | Total Class | SO Only
|  | % of Class @ Secondary | 0% | 0%
|  | % of Class @ Primary | 43.96% | 37.52%
|  | % of Class @ Sub-Transmission | 49.34% | 55.17%
|  | % of Class @ Transmission | 6.7% | 7.31%
|  |  | 100% | 100%
Large Class Weighted Average Loss Factor |  |  | 0.042414 | 0.040469
Application of Loss Factors
Total MWh to be provided = (1+loss factor) x (MWh measured at meter)
Example: | Usage @ meter = 9,700 MWh
| Total MWh to be provided = 9,700 x (1+.100169) = |  | 10671.6393