02		DEPARTMENT OF PROFESSIONAL AND FINANCIAL REGULATION

174		BOARD OF BOILERS AND PRESSURE VESSELS

# Chapter 14:	PRESSURE VESSELS

Summary: This Chapter establishes requirements for the design, construction, installation, inspection, and operation of pressure vessels.

# 1.	New Installations

A.	Registration and Certification

Before any pressure vessel is operated in the State of Maine, the owner of the pressure vessel must register the pressure vessel with the Board and must obtain a current, valid inspection certificate for the pressure vessel.

B.	Installation Inspections

(1)	Notification. The owner of a pressure vessel must notify the State and the owner’s insurance company when applicable before placing a new vessel in service.

(2)	Inspection. An Inspector must conduct the initial inspection of a pressure vessel in accordance with the applicable code specified in Chapter 11 of these rules. The initial inspection must consist of an internal and external inspection, if construction permits. The Inspector must report the results of the inspection to the Board on forms provided by the Board.

# C.	Relocation. Before a relocated pressure vessel is installed, the owner must petition the Chief Inspector for a variance to approve the installation. The Chief Inspector must perform the initial inspection of a relocated pressure vessel.

# 2.	Existing Pressure Vessels

A.	If an existing pressure vessel has not yet been registered, an Inspector must perform an initial inspection to determine the vessel’s external condition and the adequacy of the safety relieving devices. The Inspector must submit a report of inspection to the Chief Inspector on a form provided by the Board.

B.	Any pressure vessel installed and operated after July 1, 1998, must be constructed to ASME code and must be stamped and registered with the National Board. The owner of any such pressure vessel not constructed to ASME Code or stamped or registered with the National Board may seek to register the pressure vessel with the Board only by petitioning the Board for a variance.

C.	Any pressure vessel installed between June 30, 1974, and July 1, 1998, must be constructed to ASME Code. The owner of any such pressure vessel not constructed to ASME Code may seek to register the pressure vessel with the Board only by petitioning the Board for a variance.

# D.	Any pressure vessel installed before June 30, 1974, must be adequately designed for its intended use. An owner seeking to register such a pressure vessel must provide the Chief Inspector with a copy of the manufacturer’s data report relating to the vessel, a copy of the construction details with material specifications, and any other information or materials requested by the Chief Inspector.

# 3.	Periodic Inspections of Pressure Vessels

A.	Inspection Methods and Frequency. Before the initial inspection certificate expires, and every 3 years thereafter, all pressure vessels in the State must be inspected as follows:

(1)	An Inspector must perform a certificate inspection of the pressure vessel; and

(2)	The triennial certificate inspection must be internal whenever construction permits. In the event that an internal inspection is not feasible due to construction features, the Inspector must use an alternative method of determining material thickness of the shell and/or head.

B.	Report. The Inspector must submit to the Board a report of each inspection performed pursuant to Paragraph A on a form approved by the Board.

Exception: Those companies that are participating in the TAPPI Paper Machine Dryer Can Inspection Program may request permission to be issued an inspection certificate from the Board upon verification by the Authorized Inspector that the company is adhering to the TAPPI standards.

# 4.	Registration Numbers

A.	Display; Not Transferable. The assigned State of Maine registration number must appear on each pressure vessel at all times. The registration number assigned to a pressure vessel may not be transferred to another pressure vessel.

B.	Registration Number. The Inspector must place the assigned State of Maine registration number, preceded by the letters “PV,” on a self-locking metal tag issued by the Board and must affix the tag in the vicinity of the manufacturer’s name plate.

C.	Group of Pressure Vessels. For purposes of assignment of a registration number, the Board may consider a group of pressure vessels, such as the rolls of a paper machine or a dryer operating as a single machine or unit, to be one pressure vessel. In that event, the group of pressure vessels must be assigned a single master registration number and the individual pressure vessels must be assigned separate registration numbers related to the master registration number. The owner must pay a certificate fee for only a single pressure vessel.

5.	MAWP of Existing Pressure Vessels Not Constructed to Code

The MAWP on the shell of a pressure vessel or drum shall be determined by the strength of the weakest course computed from the thickness of the plate, the tensile strength of the plate, the efficiency of the longitudinal joint, the inside diameter of the course, and the factor of safety allowed by paragraph A. The formula for determining MAWP is as follows:

# TStE = MAWP, PSIG

# RFS

# Where:

TS	= 	Ultimate tensile strength of shell plates, PSI

R	= 	Inside radius of the weakest course of the shell or drum, inches.

T	= 	Minimum thickness of shell plates in weakest course, inches.

E	= 	Efficiency of longitudinal joint, as calculated in the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of the Board’s rules.

FS	= 	Factor of Safety allowed by paragraph A.

A.	Factor of Safety. The factor of safety must be at least 5.

B.	Tensile Strength. When the tensile strength of steel or wrought-iron shell plates is not known, it must be assumed to be 55,000 PSI for steel and 45,000 PSI for wrought iron.

C.	Strength of Rivets. Calculations concerning riveted joints must be those established by the ASME Boiler and Pressure Vessel Code specified in Chapter 11 of these rules, or as approved by the Board.

6.	Ten or More Pressure Vessels

Whenever 10 or more pressure vessels are installed at a plant, the owner must comply with Chapter 21(10)(B) of these rules.

7.	Modified Pressure Vessels

When any major pressure retaining item is changed on an existing pressure vessel, the change must be considered an alteration as set forth in Chapter 15.

# AUTHORITY: 32 MRSA § 15104-A(1) and § 15109(8)

# REPEALED AND REPLACED:

# January 15, 2005 -	filing 2005-26 repealed old Chapter 14

# filing 2005-27 adopted new Chapter 14